## PEMC Requirements
Req. # | Task | Status | Note
1 | BMS to PEMC communication |  | BMS acts as RS485 master and PEMC as slave; PEMC responds to BMS requests and does not initiate transactions on this link.
2 | PEMC to EM communication |  | PEMC acts as RS485 master and polls the Energy Meter (EM) as slave using the configured EM slave ID and serial settings.
3 | Support different EM modules/register maps |  | BMS configures the register address for each required reading so different EM models/sites can be supported.
4 | Read energy values |  | Read available kWh and kVAh values for Mains, DG Set, and Solar using the configured address map.
5 | Store readings in EEPROM |  | Store collected EM readings in reserved EEPROM space, retaining source, measurement, and supported time/sequence information.
6 | Separate EM and BMS records |  | Store EM readings separately from BMS-supplied settings/state in separate EEPROM address ranges.
7 | Transfer stored readings to BMS |  | Allow BMS to request stored readings and return them over the BMS-master RS485 link; record format, batch size, and acknowledgement are to be defined.
8 | Obtain and retain BMS values |  | Obtain and persist device ID, Mains/DG/Solar unit rates, prepaid balance, balance threshold, relay command, and other accepted configuration.
9 | Maintain operating state |  | Maintain device ID, current balance, relay state, unit rates, source-wise consumption, low-balance alert, threshold, BMS relay-control bit, and disconnect reason.
10 | Configure fault parameters |  | Accept, store, and apply BMS fault-monitoring parameters; names, ranges, defaults, and behavior need definition in the register map.
11 | Configure EM communication |  | Allow BMS to configure EM slave ID, baud rate, and parity; store and apply these settings for EM communication.
12 | Configure EM reading addresses |  | Allow BMS to configure and persist the EM register address for each required Mains/DG/Solar kWh/kVAh value.
13 | Clock synchronization |  | Allow BMS to synchronize PEMC clock for timestamped records/events, including enclosure-open events.
14 | LCD backlight timeout |  | Allow BMS to configure LCD backlight-on duration in seconds and turn off the backlight according to final UI behavior.
15 | Heartbeat |  | Support heartbeat command/response so BMS can check whether PEMC is communicating and responsive.
16 | Calculate consumption and balance |  | Track Mains/DG/Solar consumption, apply unit rates, and reduce prepaid balance using selected calculation source (PEMC, BMS, or both); exact formula/source behavior needs definition.
17 | Low-balance alert |  | Raise a low-balance alert when balance reaches or falls below the configured threshold and expose the status to BMS.
18 | Disconnect when balance is exhausted |  | When balance reaches zero, turn the controlled relay OFF subject to control rules and record disconnect reason and relay state.
19 | BMS override at low balance |  | Allow BMS to command relay ON and continue supply at low balance; report resulting relay status to BMS.
20 | Behavior during BMS communication loss |  | After the configured long timeout without BMS communication, allow supply to remain connected or be connected even at low balance; timeout and override priority need definition.
21 | Load- and time-based disconnection |  | Support disconnection based on configured load conditions and elapsed time; thresholds, timing, and priority need definition.
22 | Consumption after disconnection |  | If relay is OFF but consumption continues, raise a fault alarm and report it to BMS; detection threshold and confirmation interval are configurable.
23 | Loss of EM communication |  | Raise and report a communication fault if PEMC cannot communicate with EM; retry count and timeout must be configured or specified.
24 | Enclosure tamper event |  | Detect enclosure opening, set tamper flag, retain timestamps of the five most recent opening events, and make flag/history readable by BMS.
25 | Define BMS↔PEMC RS485 register map |  | Define protocol, register numbers, data types, scaling, byte/word order, error codes, and command acknowledgement behavior.
26 | Define PEMC↔EM RS485 register map |  | Define protocol, register numbers, data types, scaling, byte/word order, error codes, and command acknowledgement behavior.
27 | Define EEPROM allocation and retention |  | Specify EEPROM ranges, write frequency, record capacity, retention, and behavior when storage is full.
28 | Define balance accounting formula |  | Specify meter reset/rollover handling and how Mains/DG/Solar consumption is attributed and priced.
29 | Define threshold and timeout behavior |  | Specify threshold comparison, BMS-loss timeout, EM retry/timeout, and load/time disconnection limits.
30 | Define relay-control priority |  | Specify precedence among prepaid rules, BMS command, communication loss, load/time rules, and faults.
31 | Define tamper and clock behavior |  | Specify tamper input behavior, timestamp format, clock-loss handling, and exact LCD backlight timeout behavior.